## Sheet1
QEI Point ID | Station | Point | Description | Comm | RTU | Page | Point | Analog # | Relay | Relay | Scale Factor | Point Type | HELPER COLUMN | IP | DNP Address | DNP Point #
30116 | ME | 4BF | ME BKR 4 BKR FAIL | 1 | 11 | 6 | 8 |  |  |  |  | STATUS | ME4BFSTATUS | 172.16.3.81 | 1 | 107
30224 | ME | 1BF | ME BKR 1 BKR FAIL | 1 | 11 | 6 | 5 |  |  |  |  | STATUS | ME1BFSTATUS | 172.16.3.81 | 1 | 71
30227 | ME | 3BF | ME BKR 3 BKR FAIL | 1 | 11 | 6 | 7 |  |  |  |  | STATUS | ME3BFSTATUS | 172.16.3.81 | 1 | 95
30705 | ME | 1 | ME FEEDER BKR 1 | 1 | 11 | 0 | 0 |  |  |  |  | STATUS | ME1STATUS | 172.16.3.81 | 1 | 66
30705 | ME | 1 | BRK #1 OPEN | 1 | 11 |  |  |  | 0 | 1 |  | RELAY | ME1RELAY | 172.16.3.81 | 1 | 18
30705 | ME | 1 | BRK #1 CLOSE | 1 | 11 |  |  |  | 0 | 0 |  | RELAY | ME1RELAY | 172.16.3.81 | 1 | 18
30706 | ME | 2 | ME FEEDER BKR 2 | 1 | 11 | 0 | 4 |  |  |  |  | STATUS | ME2STATUS | 172.16.3.81 | 1 | 78
30706 | ME | 2 | BRK #2 TRIP | 1 | 11 |  |  |  | 4 | 1 |  | RELAY | ME2RELAY | 172.16.3.81 | 1 | 23
30706 | ME | 2 | BRK #2 CLOSE | 1 | 11 |  |  |  | 4 | 0 |  | RELAY | ME2RELAY | 172.16.3.81 | 1 | 23
30707 | ME | 4 | ME FEEDER BKR 4 | 1 | 11 | 0 | 12 |  |  |  |  | STATUS | ME4STATUS | 172.16.3.81 | 1 | 102
30707 | ME | 4 | BRK #4 TRIP | 1 | 11 |  |  |  | 12 | 1 |  | RELAY | ME4RELAY | 172.16.3.81 | 1 | 33
30707 | ME | 4 | BRK #4 CLOSE | 1 | 11 |  |  |  | 12 | 0 |  | RELAY | ME4RELAY | 172.16.3.81 | 1 | 33
30708 | ME | 1R | ME BKR 1 RECLOSER | 1 | 11 | 0 | 1 |  |  |  |  | STATUS | ME1RSTATUS | 172.16.3.81 | 1 | 67
30708 | ME | 1R | BKR #1 RECLOSE OFF | 1 | 11 |  |  |  | 1 | 1 |  | RELAY | ME1RRELAY | 172.16.3.81 | 1 | 19
30708 | ME | 1R | BKR #1 RECLOSE ON | 1 | 11 |  |  |  | 1 | 0 |  | RELAY | ME1RRELAY | 172.16.3.81 | 1 | 19
30709 | ME | 2R | ME BKR 2 RECLOSER | 1 | 11 | 0 | 5 |  |  |  |  | STATUS | ME2RSTATUS | 172.16.3.81 | 1 | 79
30709 | ME | 2R | BRK #2 RECLOSE OFF | 1 | 11 |  |  |  | 5 | 1 |  | RELAY | ME2RRELAY | 172.16.3.81 | 1 | 24
30709 | ME | 2R | BRK #2 RECLOSE ON | 1 | 11 |  |  |  | 5 | 0 |  | RELAY | ME2RRELAY | 172.16.3.81 | 1 | 24
30710 | ME | 4R | ME BKR 4 RECLOSER | 1 | 11 | 0 | 13 |  |  |  |  | STATUS | ME4RSTATUS | 172.16.3.81 | 1 | 103
30710 | ME | 4R | BKR 4 RECLOSE OFF | 1 | 11 |  |  |  | 13 | 1 |  | RELAY | ME4RRELAY | 172.16.3.81 | 1 | 34
30710 | ME | 4R | BKR 4 RECLOSE ON | 1 | 11 |  |  |  | 13 | 0 |  | RELAY | ME4RRELAY | 172.16.3.81 | 1 | 34
30714 | ME | 1GT | ME BKR 1 GRND TRIP BLOCK | 1 | 11 | 0 | 2 |  |  |  |  | STATUS | ME1GTSTATUS | 172.16.3.81 | 1 | 68
30714 | ME | 1GT | BRK #1 GND TRIP DISABLED | 1 | 11 |  |  |  | 2 | 1 |  | RELAY | ME1GTRELAY | 172.16.3.81 | 1 | 20
30714 | ME | 1GT | BRK #1 GND TRIP ENABLED | 1 | 11 |  |  |  | 2 | 0 |  | RELAY | ME1GTRELAY | 172.16.3.81 | 1 | 20
30715 | ME | 1LR | ME BKR 1 LOC/REM SW | 1 | 11 | 0 | 3 |  |  |  |  | STATUS | ME1LRSTATUS | 172.16.3.81 | 1 | 69
30716 | ME | 2GT | ME BKR 2 GRND TRIP BLOCK | 1 | 11 | 0 | 6 |  |  |  |  | STATUS | ME2GTSTATUS | 172.16.3.81 | 1 | 80
30716 | ME | 2GT | BRK #2 GND TRIP DISABLED | 1 | 11 |  |  |  | 6 | 1 |  | RELAY | ME2GTRELAY | 172.16.3.81 | 1 | 25
30716 | ME | 2GT | BRK #2 GND TRIP ENABLED | 1 | 11 |  |  |  | 6 | 0 |  | RELAY | ME2GTRELAY | 172.16.3.81 | 1 | 25
30717 | ME | 2LR | ME BKR 2 LOC/REM SW | 1 | 11 | 0 | 7 |  |  |  |  | STATUS | ME2LRSTATUS | 172.16.3.81 | 1 | 81
30718 | ME | 3 | ME FEEDER BKR 3 | 1 | 11 | 0 | 8 |  |  |  |  | STATUS | ME3STATUS | 172.16.3.81 | 1 | 90
30718 | ME | 3 | BRK #3 TRIP | 1 | 11 |  |  |  | 8 | 1 |  | RELAY | ME3RELAY | 172.16.3.81 | 1 | 28
30718 | ME | 3 | BRK #3 CLOSE | 1 | 11 |  |  |  | 8 | 0 |  | RELAY | ME3RELAY | 172.16.3.81 | 1 | 28
30741 | ME | 3R | ME BKR 3 RECLOSER | 1 | 11 | 0 | 9 |  |  |  |  | STATUS | ME3RSTATUS | 172.16.3.81 | 1 | 91
30741 | ME | 3R | BRK #3 RECLOSE OFF | 1 | 11 |  |  |  | 9 | 1 |  | RELAY | ME3RRELAY | 172.16.3.81 | 1 | 29
30741 | ME | 3R | BRK #3 RECLOSE ON | 1 | 11 |  |  |  | 9 | 0 |  | RELAY | ME3RRELAY | 172.16.3.81 | 1 | 29
31634 | ME | TX1DRD | DIFFERENTIAL RELAY DISAB | 1 | 11 | 6 | 0 |  |  |  |  | STATUS | METX1DRDSTATUS | 172.16.3.81 | 1 | 194
31636 | ME | MTXAC | MOBIL TX LOSS OF AC | 1 | 11 | 7 | 0 |  |  |  |  | STATUS | MEMTXACSTATUS | 172.16.3.81 | 1 | #N/A
32208 | ME | 3GT | ME BKR 3 GRND TRIP BLOCK | 1 | 11 | 0 | 10 |  |  |  |  | STATUS | ME3GTSTATUS | 172.16.3.81 | 1 | 92
32208 | ME | 3GT | BRK #3 GROUND TRIP DISABLED | 1 | 11 |  |  |  | 10 | 1 |  | RELAY | ME3GTRELAY | 172.16.3.81 | 1 | 30
32208 | ME | 3GT | BRK #3 GROUND TRIP ENABLED | 1 | 11 |  |  |  | 10 | 0 |  | RELAY | ME3GTRELAY | 172.16.3.81 | 1 | 30
33187 | ME | TX1K1 | ME TX1 VOLT CONTROL K1 | 1 | 11 | 2 | 4 |  |  |  |  | STATUS | METX1K1STATUS | 172.16.3.81 | 1 | 52
33187 | ME | TX1K1 | TX VOLT CONTROL K1 SET | 1 | 11 |  |  |  | 21 | 1 |  | RELAY | METX1K1RELAY | 172.16.3.81 | 1 | 9
33187 | ME | TX1K1 | TX VOLT CONTROL K1 RESET | 1 | 11 |  |  |  | 21 | 0 |  | RELAY | METX1K1RELAY | 172.16.3.81 | 1 | 9
33188 | ME | TX1K2 | ME TX1 VOLT CONTROL K2 | 1 | 11 | 2 | 5 |  |  |  |  | STATUS | METX1K2STATUS | 172.16.3.81 | 1 | 53
33188 | ME | TX1K2 | TX1 VOLT CONTROL K2 SET | 1 | 11 |  |  |  | 22 | 1 |  | RELAY | METX1K2RELAY | 172.16.3.81 | 1 | 10
33188 | ME | TX1K2 | TX1 VOLT CONTROL K2 RESET | 1 | 11 |  |  |  | 22 | 0 |  | RELAY | METX1K2RELAY | 172.16.3.81 | 1 | 10
33230 | ME | 35C106 | ME TX1 387E ALARM COMM | 1 | 11 | 1 | 0 |  |  |  |  | STATUS | ME35C106STATUS | 172.16.3.81 | 1 | 119
34002 | ME | MTXSC | MOBIL TX SELF CK | 1 | 11 | 7 | 2 |  |  |  |  | STATUS | MEMTXSCSTATUS | 172.16.3.81 | 1 | #N/A
34268 | ME | MTXTOT | MOBIL TX HOT OIL TEMP | 1 | 11 | 7 | 1 |  |  |  |  | STATUS | MEMTXTOTSTATUS | 172.16.3.81 | 1 | #N/A
34992 | ME | 3LR | ME BKR 3 LOC/REM SW | 1 | 11 | 0 | 11 |  |  |  |  | STATUS | ME3LRSTATUS | 172.16.3.81 | 1 | 93
34993 | ME | 4GT | ME BKR 4 GRND TRIP BLOCK | 1 | 11 | 0 | 14 |  |  |  |  | STATUS | ME4GTSTATUS | 172.16.3.81 | 1 | 104
34993 | ME | 4GT | BKR 4 GND TRIP DISABLED | 1 | 11 |  |  |  | 14 | 1 |  | RELAY | ME4GTRELAY | 172.16.3.81 | 1 | 35
34993 | ME | 4GT | BKR 4 GND TRIP ENABLED | 1 | 11 |  |  |  | 14 | 0 |  | RELAY | ME4GTRELAY | 172.16.3.81 | 1 | 35
34994 | ME | 4LR | ME BKR 4 LOC/REM SW | 1 | 11 | 0 | 15 |  |  |  |  | STATUS | ME4LRSTATUS | 172.16.3.81 | 1 | 105
34995 | ME | 351SC1 | ME BKR 1 RELAY FAIL | 1 | 11 | 1 | 1 |  |  |  |  | STATUS | ME351SC1STATUS | 172.16.3.81 | 1 | 188
34996 | ME | 351SC2 | ME BKR 2 RELAY FAIL | 1 | 11 | 1 | 2 |  |  |  |  | STATUS | ME351SC2STATUS | 172.16.3.81 | 1 | 189
34997 | ME | 351SC3 | ME BKR 3 RELAY FAIL | 1 | 11 | 1 | 3 |  |  |  |  | STATUS | ME351SC3STATUS | 172.16.3.81 | 1 | 190
34998 | ME | 351SC4 | ME BKR 4 RELAY FAIL | 1 | 11 | 1 | 4 |  |  |  |  | STATUS | ME351SC4STATUS | 172.16.3.81 | 1 | 191
34999 | ME | 35C118 | ME BKR 1 STATUS COMM | 1 | 11 | 1 | 5 |  |  |  |  | STATUS | ME35C118STATUS | 172.16.3.81 | 1 | 131
35000 | ME | 35C119 | ME BKR 2 STATUS COMM | 1 | 11 | 1 | 6 |  |  |  |  | STATUS | ME35C119STATUS | 172.16.3.81 | 1 | 132
35001 | ME | 35C120 | ME BKR 3 STATUS COMM | 1 | 11 | 1 | 7 |  |  |  |  | STATUS | ME35C120STATUS | 172.16.3.81 | 1 | 133
35002 | ME | 35C121 | ME BKR 4 STATUS COMM | 1 | 11 | 1 | 8 |  |  |  |  | STATUS | ME35C121STATUS | 172.16.3.81 | 1 | 134
35003 | ME | 35C123 | TX1 2505 STAT/CNTRL COMM | 1 | 11 | 1 | 9 |  |  |  |  | STATUS | ME35C123STATUS | 172.16.3.81 | 1 | 136
35004 | ME | 35C126 | HOUSE 2505 SELF CHECK | 1 | 11 | 1 | 10 |  |  |  |  | STATUS | ME35C126STATUS | 172.16.3.81 | 1 | 139
35005 | ME | 35C128 | ME TX1 FUTURE COMM | 1 | 11 | 1 | 11 |  |  |  |  | STATUS | ME35C128STATUS | 172.16.3.81 | 1 | 141
35007 | ME | 24T1SC | ME TX1 2411 ALARMS FAIL | 1 | 11 | 2 | 0 |  |  |  |  | STATUS | ME24T1SCSTATUS | 172.16.3.81 | 1 | 184
35007 | ME | TX1TOT | ME TX1 HOT OIL TEMP | 1 | 11 | 2 | 1 |  |  |  |  | STATUS | METX1TOTSTATUS | 172.16.3.81 | 1 | 49
35008 | ME | TX1HS | ME TX1 HOT SPOT | 1 | 11 | 2 | 2 |  |  |  |  | STATUS | METX1HSSTATUS | 172.16.3.81 | 1 | 50
35009 | ME | TX1LR | ME TX1 LOC/REM SW | 1 | 11 | 2 | 3 |  |  |  |  | STATUS | METX1LRSTATUS | 172.16.3.81 | 1 | 51
35010 | ME | TCA1 | ME TX1 LTC AUTO/MAN | 1 | 11 | 2 | 6 |  |  |  |  | STATUS | METCA1STATUS | 172.16.3.81 | 1 | 54
35010 | ME | TCA1 | TX LTC MANUAL | 1 | 11 |  |  |  | 20 | 1 |  | RELAY | METCA1RELAY | 172.16.3.81 | 1 | 8
35010 | ME | TCA1 | TX LTC AUTO | 1 | 11 |  |  |  | 20 | 0 |  | RELAY | METCA1RELAY | 172.16.3.81 | 1 | 8
35011 | ME | FANHYD | HOUSE EXHAUST FAN HYRDRO | 1 | 11 | 2 | 7 |  |  |  |  | STATUS | MEFANHYDSTATUS | 172.16.3.81 | 1 | 208
35012 | ME | SMOKE | ME HOUSE SMOKE | 1 | 11 | 2 | 8 |  |  |  |  | STATUS | MESMOKESTATUS | 172.16.3.81 | 1 | 209
35014 | ME | BATPWR | ME BATT POWER FAIL | 1 | 11 | 2 | 10 |  |  |  |  | STATUS | MEBATPWRSTATUS | 172.16.3.81 | 1 | 210
35015 | ME | BATTDC | ME BATT DC VOLT | 1 | 11 | 2 | 11 |  |  |  |  | STATUS | MEBATTDCSTATUS | 172.16.3.81 | 1 | 211
35016 | ME | BATGND | ME BATT GROUND | 1 | 11 | 2 | 12 |  |  |  |  | STATUS | MEBATGNDSTATUS | 172.16.3.81 | 1 | 212
35017 | ME | LRS | SUB LOC/REM SW | 1 | 11 | 3 | 0 |  |  |  |  | STATUS | MELRSSTATUS | 172.16.3.81 | 1 | 193
35018 | ME | 86T1 | ME TX1 86T LCKOUT | 1 | 11 | 3 | 1 |  |  |  |  | STATUS | ME86T1STATUS | 172.16.3.81 | 1 | 195
35019 | ME | 387SC1 | ME TX1 DIF PROT FAIL | 1 | 11 | 3 | 2 |  |  |  |  | STATUS | ME387SC1STATUS | 172.16.3.81 | 1 | 171
35020 | ME | 501SC1 | ME TX1 OVERCURRENT FAIL | 1 | 11 | 3 | 3 |  |  |  |  | STATUS | ME501SC1STATUS | 172.16.3.81 | 1 | 172
35021 | ME | 21T1SC | ME TX1 2100 FAIL | 1 | 11 | 3 | 4 |  |  |  |  | STATUS | ME21T1SCSTATUS | 172.16.3.81 | 1 | 175
35022 | ME | MET1SC | ME TX1 METER FAIL | 1 | 11 | 3 | 5 |  |  |  |  | STATUS | MEMET1SCSTATUS | 172.16.3.81 | 1 | 176
35023 | ME | 86TCM1 | ME TX1 86T LCKOUT TCM | 1 | 11 | 3 | 6 |  |  |  |  | STATUS | ME86TCM1STATUS | 172.16.3.81 | 1 | 196
35024 | ME | 94TCM1 | ME TX1 94T TCM | 1 | 11 | 3 | 7 |  |  |  |  | STATUS | ME94TCM1STATUS | 172.16.3.81 | 1 | 201
35025 | ME | K697 | ME K697 CIRC SW | 1 | 11 | 3 | 8 |  |  |  |  | STATUS | MEK697STATUS | 172.16.3.81 | 1 | 0
35025 | ME | K697 | CIRCUIT SWITCHER TRIP | 1 | 11 |  |  |  | 16 | 1 |  | RELAY | MEK697RELAY | 172.16.3.81 | 1 | 0
35025 | ME | K697 | CIRCUIT SWITCHER CLOSE | 1 | 11 |  |  |  | 16 | 0 |  | RELAY | MEK697RELAY | 172.16.3.81 | 1 | 0
35026 | ME | 25SC10 | ME CH STA/CTRL FAIL | 1 | 11 | 3 | 10 |  |  |  |  | STATUS | ME25SC10STATUS | 172.16.3.81 | 1 | 181
35027 | ME | 35C109 | TX1 3530 TO 2100 COMM | 1 | 11 | 7 | 3 |  |  |  |  | STATUS | ME35C109STATUS | 172.16.3.81 | 1 | 122
35028 | ME | 35C101 | ME BKR 1 CONTROL COMM | 1 | 11 | 3 | 12 |  |  |  |  | STATUS | ME35C101STATUS | 172.16.3.81 | 1 | 114
35029 | ME | 35C102 | ME BKR 2 CONTROL COMM | 1 | 11 | 3 | 13 |  |  |  |  | STATUS | ME35C102STATUS | 172.16.3.81 | 1 | 115
35030 | ME | 35C103 | ME BKR 3 CONTROL COMM | 1 | 11 | 3 | 14 |  |  |  |  | STATUS | ME35C103STATUS | 172.16.3.81 | 1 | 116
35031 | ME | 35C104 | ME BKR 4 CONTROL COMM | 1 | 11 | 3 | 15 |  |  |  |  | STATUS | ME35C104STATUS | 172.16.3.81 | 1 | 117
35033 | ME | T1F1AC | ME TX STG1 FANS LOSS AC | 1 | 11 | 4 | 0 |  |  |  |  | STATUS | MET1F1ACSTATUS | 172.16.3.81 | 1 | 31
35034 | ME | T1F2AC | ME TX STG2 FANS LOSS AC | 1 | 11 | 4 | 1 |  |  |  |  | STATUS | MET1F2ACSTATUS | 172.16.3.81 | 1 | 32
35035 | ME | TX1NHI | ME TX1 NITRO HIGH PR | 1 | 11 | 4 | 2 |  |  |  |  | STATUS | METX1NHISTATUS | 172.16.3.81 | 1 | 33
35036 | ME | TX1NLO | ME TX NITRO LOW PR | 1 | 11 | 4 | 3 |  |  |  |  | STATUS | METX1NLOSTATUS | 172.16.3.81 | 1 | 34
35037 | ME | T1NCLO | ME TX1 NITRO CYL LOW PR | 1 | 11 | 4 | 4 |  |  |  |  | STATUS | MET1NCLOSTATUS | 172.16.3.81 | 1 | 35
35038 | ME | T1PR | ME TX1 TANK PRS RELIEF | 1 | 11 | 4 | 5 |  |  |  |  | STATUS | MET1PRSTATUS | 172.16.3.81 | 1 | 36
35099 | ME | 1UF | ME BKR 1 UNDER FREQ TRIP | 1 | 11 | 1 | 13 |  |  |  |  | STATUS | ME1UFSTATUS | 172.16.3.81 | 1 | 70
35100 | ME | 3UF | ME BKR 3 UNDER FREQ TRIP | 1 | 11 | 1 | 14 |  |  |  |  | STATUS | ME3UFSTATUS | 172.16.3.81 | 1 | 94
35101 | ME | 1POT | ME BKR 1 LOSS POT FOR UF | 1 | 11 | 1 | 15 |  |  |  |  | STATUS | ME1POTSTATUS | 172.16.3.81 | 1 | 73
35102 | ME | 2POT | ME BKR 2 LOSS POT FOR UF | 1 | 11 | 2 | 13 |  |  |  |  | STATUS | ME2POTSTATUS | 172.16.3.81 | 1 | 85
35103 | ME | 3POT | ME BKR 3 LOSS POT FOR UF | 1 | 11 | 2 | 14 |  |  |  |  | STATUS | ME3POTSTATUS | 172.16.3.81 | 1 | 97
35104 | ME | 4POT | ME BKR 4 LOSS POT FOR UF | 1 | 11 | 2 | 15 |  |  |  |  | STATUS | ME4POTSTATUS | 172.16.3.81 | 1 | 109
35220 | ME | S3L12 | ME LBI S3L12 | 1 | 11 | 3 | 9 |  |  |  |  | STATUS | MES3L12STATUS | 172.16.3.81 | 1 | 64
35220 | ME | S3L12 | S3L12 LBI OPEN | 1 | 11 |  |  |  | 17 | 1 |  | RELAY | MES3L12RELAY | 172.16.3.81 | 1 | 17
35220 | ME | S3L12 | S3L12 LBI CLOSE | 1 | 11 |  |  |  | 17 | 0 |  | RELAY | MES3L12RELAY | 172.16.3.81 | 1 | 17
35235 | ME | T1SP | ME TX1 TANK SUDDEN PRS | 1 | 11 | 4 | 6 |  |  |  |  | STATUS | MET1SPSTATUS | 172.16.3.81 | 1 | 37
35236 | ME | TX1LO | ME TX1 TANK LO OIL | 1 | 11 | 4 | 7 |  |  |  |  | STATUS | METX1LOSTATUS | 172.16.3.81 | 1 | 38
35237 | ME | TX1HI | ME TX1 TANK HI OIL | 1 | 11 | 4 | 8 |  |  |  |  | STATUS | METX1HISTATUS | 172.16.3.81 | 1 | 39
35238 | ME | LTC1LO | ME TX1 LTC TANK LO OIL | 1 | 11 | 4 | 9 |  |  |  |  | STATUS | MELTC1LOSTATUS | 172.16.3.81 | 1 | 41
35239 | ME | TC1PWR | ME TX1 LTC LOSS OF POWER | 1 | 11 | 4 | 10 |  |  |  |  | STATUS | METC1PWRSTATUS | 172.16.3.81 | 1 | 42
35240 | ME | TCP1 | ME TX1 LTC OFF TAP | 1 | 11 | 4 | 11 |  |  |  |  | STATUS | METCP1STATUS | 172.16.3.81 | 1 | 43
35241 | ME | LTCMT1 | ME TX1 LTC MOTOR HI TEMP | 1 | 11 | 4 | 12 |  |  |  |  | STATUS | MELTCMT1STATUS | 172.16.3.81 | 1 | 44
35242 | ME | TCPR1 | ME TX1 LTC PRS RELIEF | 1 | 11 | 4 | 13 |  |  |  |  | STATUS | METCPR1STATUS | 172.16.3.81 | 1 | 45
35243 | ME | 86X1 | ME TX1 LTC LCKOUT | 1 | 11 | 4 | 14 |  |  |  |  | STATUS | ME86X1STATUS | 172.16.3.81 | 1 | 46
35244 | ME | T1FAN1 | ME TX1 STAGE1 FANS ON | 1 | 11 | 4 | 15 |  |  |  |  | STATUS | MET1FAN1STATUS | 172.16.3.81 | 1 | 47
35244 | ME | T1FAN1 | TX STAGE 1 FANS OFF | 1 | 11 |  |  |  | 18 | 1 |  | RELAY | MET1FAN1RELAY | 172.16.3.81 | 1 | 6
35244 | ME | T1FAN1 | TX STAGE 1 FANS ON | 1 | 11 |  |  |  | 18 | 0 |  | RELAY | MET1FAN1RELAY | 172.16.3.81 | 1 | 6
35245 | ME | T1FAN2 | ME TX1 STAGE2 FANS ON | 1 | 11 | 5 | 0 |  |  |  |  | STATUS | MET1FAN2STATUS | 172.16.3.81 | 1 | 48
35245 | ME | T1FAN2 | TX STAGE 2 FANS OFF | 1 | 11 |  |  |  | 19 | 1 |  | RELAY | MET1FAN2RELAY | 172.16.3.81 | 1 | 7
35245 | ME | T1FAN2 | TX STAGE 2 FANS ON | 1 | 11 |  |  |  | 19 | 0 |  | RELAY | MET1FAN2RELAY | 172.16.3.81 | 1 | 7
35246 | ME | 35C111 | ME TX1 ALARMS COMM | 1 | 11 | 5 | 1 |  |  |  |  | STATUS | ME35C111STATUS | 172.16.3.81 | 1 | 124
35302 | ME | 2UF | ME BKR 2 UNDER FREQ TRIP | 1 | 11 | 2 | 9 |  |  |  |  | STATUS | ME2UFSTATUS | 172.16.3.81 | 1 | 82
35918 | ME | 2BF | ME BKR 2 BKR FAIL | 1 | 11 | 6 | 6 |  |  |  |  | STATUS | ME2BFSTATUS | 172.16.3.81 | 1 | 83
36609 | ME | MET1CP | ME TX1 METERING COMM | 1 | 11 | 5 | 2 |  |  |  |  | STATUS | MEMET1CPSTATUS | 172.16.3.81 | 1 | 121
36896 | ME | 79LO1 | ME BKR 1 LCKOUT | 1 | 11 | 5 | 3 |  |  |  |  | STATUS | ME79LO1STATUS | 172.16.3.81 | 1 | 74
36897 | ME | 79LO2 | ME BKR 2 LCKOUT | 1 | 11 | 5 | 4 |  |  |  |  | STATUS | ME79LO2STATUS | 172.16.3.81 | 1 | 86
36898 | ME | 79LO3 | ME BKR 1 LCKOUT | 1 | 11 | 5 | 5 |  |  |  |  | STATUS | ME79LO3STATUS | 172.16.3.81 | 1 | 98
36899 | ME | 79LO4 | ME BKR 4 LCKOUT | 1 | 11 | 5 | 6 |  |  |  |  | STATUS | ME79LO4STATUS | 172.16.3.81 | 1 | 110
37285 | ME | 1HL | ME BKR 1 HL NON-RECL | 1 | 11 | 6 | 1 |  |  |  |  | STATUS | ME1HLSTATUS | 172.16.3.81 | 1 | 72
37285 | ME | 1HL | BKR 1 HOT LINE REC DISABLED | 1 | 11 |  |  |  | 3 | 1 |  | RELAY | ME1HLRELAY | 172.16.3.81 | 1 | 21
37285 | ME | 1HL | BKR 1 HOT LINE REC ENABLED | 1 | 11 |  |  |  | 3 | 0 |  | RELAY | ME1HLRELAY | 172.16.3.81 | 1 | 21
37286 | ME | 2HL | ME BKR 2 HL NON-RECL | 1 | 11 | 6 | 2 |  |  |  |  | STATUS | ME2HLSTATUS | 172.16.3.81 | 1 | 84
37286 | ME | 2HL | BKR 2 HOT LINE REC DISABLED | 1 | 11 |  |  |  | 7 | 1 |  | RELAY | ME2HLRELAY | 172.16.3.81 | 1 | 26
37286 | ME | 2HL | BKR 2 HOT LINE REC ENABLED | 1 | 11 |  |  |  | 7 | 0 |  | RELAY | ME2HLRELAY | 172.16.3.81 | 1 | 26
37287 | ME | 3HL | ME BKR 3 HL NON-RECL | 1 | 11 | 6 | 3 |  |  |  |  | STATUS | ME3HLSTATUS | 172.16.3.81 | 1 | 96
37287 | ME | 3HL | BKR 3 HOT LINE REC DISABLED | 1 | 11 |  |  |  | 11 | 1 |  | RELAY | ME3HLRELAY | 172.16.3.81 | 1 | 31
37287 | ME | 3HL | BKR 3 HOT LINE REC ENABLED | 1 | 11 |  |  |  | 11 | 0 |  | RELAY | ME3HLRELAY | 172.16.3.81 | 1 | 31
37288 | ME | 4HL | ME BKR 4 HL NON-RECL | 1 | 11 | 6 | 4 |  |  |  |  | STATUS | ME4HLSTATUS | 172.16.3.81 | 1 | 108
37288 | ME | 4HL | BKR 4 HOT LINE REC DISABLED | 1 | 11 |  |  |  | 15 | 1 |  | RELAY | ME4HLRELAY | 172.16.3.81 | 1 | 36
37288 | ME | 4HL | BKR 4 HOT LINE REC ENABLED | 1 | 11 |  |  |  | 15 | 0 |  | RELAY | ME4HLRELAY | 172.16.3.81 | 1 | 36
38177 | ME | 35C110 | ME 2100-1 ALARM COMM | 1 | 11 | 7 | 4 |  |  |  |  | STATUS | ME35C110STATUS | 172.16.3.81 | 1 | 123
38178 | ME | 35C116 | 3530-1 DNP COMM PORT ALARM | 1 | 11 | 6 | 10 |  |  |  |  | STATUS | ME35C116STATUS | 172.16.3.81 | 1 | #N/A
38179 | ME | 2407SC | CLOCK SELF CHECK | 1 | 11 | 6 | 11 |  |  |  |  | STATUS | ME2407SCSTATUS | 172.16.3.81 | 1 | 177
38350 | ME | T1HIAL | ME TX1 CRIT HI TEMP AL | 1 | 11 | 3 | 11 |  |  |  |  | STATUS | MET1HIALSTATUS | 172.16.3.81 | 1 | 56
05592 | ME | 1B | ME BKR 1B AMPS BKR TRIP | 1 | 11 |  |  | 17 |  |  | .29311187 | ANALOG | ME1BANALOG | 172.16.3.81 | 1 | 47
05593 | ME | 3PF | ME FDR 3 POWER FACTOR | 1 | 11 |  |  | 38 |  |  | 0.1 | ANALOG | ME3PFANALOG | 172.16.3.81 | 1 | 63
05598 | ME | TX1W | MELROSE WATTS | 1 | 11 |  |  | 6 |  |  | 48 | ANALOG | METX1WANALOG | 172.16.3.81 | 1 | 31
05659 | ME | P1 | MELROSE ACCUMULATOR FPL | 1 | 11 | [5 empty] | 7.2 | PULSE | MEP1PULSE | 172.16.3.81 | 1 | #N/A
05660 | ME | RAV1 | ME REG A PH VOLTS | 1 | 11 |  |  | 0 |  |  | 0.1 | ANALOG | MERAV1ANALOG | 172.16.3.81 | 1 | 24
05661 | ME | RBV1 | ME REG B PH VOLTS | 1 | 11 | 1 |  | 1 |  |  | 0.1 | ANALOG | MERBV1ANALOG | 172.16.3.81 | 1 | 25
05832 | ME | 2A | ME BKR 2A AMPS BKR TRIP | 1 | 11 |  |  | 19 |  |  | .29311187 | ANALOG | ME2AANALOG | 172.16.3.81 | 1 | 52
05839 | ME | 2B | ME BKR 2B AMPS BKR TRIP | 1 | 11 |  |  | 20 |  |  | .29311187 | ANALOG | ME2BANALOG | 172.16.3.81 | 1 | 53
05863 | ME | 2C | ME BKR 2C AMPS BKR TRIP | 1 | 11 |  |  | 21 |  |  | .29311187 | ANALOG | ME2CANALOG | 172.16.3.81 | 1 | 54
06115 | ME | RCV1 | RCV1 | 1 | 11 | 2 |  | 2 |  |  | 0.1 | ANALOG | MERCV1ANALOG | 172.16.3.81 | 1 | 26
06215 | ME | TX1A | ME TX A AMPS C/S TRIP | 1 | 11 | 3 |  | 3 |  |  | 1.2 | ANALOG | METX1AANALOG | 172.16.3.81 | 1 | 27
06425 | ME | 1A | ME BKR 1A AMPS BKR TRIP | 1 | 11 |  |  | 16 |  |  | .29311187 | ANALOG | ME1AANALOG | 172.16.3.81 | 1 | 46
06426 | ME | 1C | ME BKR 1C AMPS BKR TRIP | 1 | 11 |  |  | 18 |  |  | .29311187 | ANALOG | ME1CANALOG | 172.16.3.81 | 1 | 48
06427 | ME | 3A | ME BKR 3A AMPS BKR TRIP | 1 | 11 |  |  | 22 |  |  | .29311187 | ANALOG | ME3AANALOG | 172.16.3.81 | 1 | 58
06428 | ME | 4PF | ME FDR 4 POWER FACTOR | 1 | 11 |  |  | 39 |  |  | 0.1 | ANALOG | ME4PFANALOG | 172.16.3.81 | 1 | 69
06600 | ME | TX1FRQ | ME FREQUENCY | 1 | 11 |  |  | 8 |  |  | 0.1 | ANALOG | METX1FRQANALOG | 172.16.3.81 | 1 | 35
06612 | ME | PF1M | ME POWER FACTOR METER | 1 | 11 |  |  | 7 |  |  | 0.1 | ANALOG | MEPF1MANALOG | 172.16.3.81 | 1 | 34
06705 | ME | 1KW | ME FDR 1 WATTS | 1 | 11 |  |  | 32 |  |  | 10 | ANALOG | ME1KWANALOG | 172.16.3.81 | 1 | 49
06709 | ME | 2KW | ME FDR 2 WATTS | 1 | 11 |  |  | 33 |  |  | 10 | ANALOG | ME2KWANALOG | 172.16.3.81 | 1 | 55
06728 | ME | 3KW | ME FDR 3 WATTS | 1 | 11 |  |  | 34 |  |  | 10 | ANALOG | ME3KWANALOG | 172.16.3.81 | 1 | 61
06729 | ME | 4KW | ME FDR 4 WATTS | 1 | 11 |  |  | 35 |  |  | 10 | ANALOG | ME4KWANALOG | 172.16.3.81 | 1 | 67
06943 | ME | KVA1M | ME KVA METER | 1 | 11 |  |  | 9 |  |  | 48 | ANALOG | MEKVA1MANALOG | 172.16.3.81 | 1 | 30
07187 | ME | TX1B | ME TX B AMPS C/S TRIP | 1 | 11 | 4 |  | 4 |  |  | 1.2 | ANALOG | METX1BANALOG | 172.16.3.81 | 1 | 28
07188 | ME | TX1C | ME TX C AMPS C/S TRIP | 1 | 11 | 5 |  | 5 |  |  | 1.2 | ANALOG | METX1CANALOG | 172.16.3.81 | 1 | 29
07196 | ME | 3B | ME BKR 3B AMPS BKR TRIP | 1 | 11 |  |  | 23 |  |  | .29311187 | ANALOG | ME3BANALOG | 172.16.3.81 | 1 | 59
07197 | ME | 3C | ME BKR 3C AMPS BKR TRIP | 1 | 11 |  |  | 24 |  |  | .29311187 | ANALOG | ME3CANALOG | 172.16.3.81 | 1 | 60
07198 | ME | 4A | ME BKR 4A AMPS BKR TRIP | 1 | 11 |  |  | 25 |  |  | .29311187 | ANALOG | ME4AANALOG | 172.16.3.81 | 1 | 64
07199 | ME | 4B | ME BKR 4B AMPS BKR TRIP | 1 | 11 |  |  | 26 |  |  | .29311187 | ANALOG | ME4BANALOG | 172.16.3.81 | 1 | 65
07200 | ME | 4C | ME BKR 4C AMPS BKR TRIP | 1 | 11 |  |  | 27 |  |  | .29311187 | ANALOG | ME4CANALOG | 172.16.3.81 | 1 | 66
07201 | ME | LTC1 | ME LD TAP CHGR POS | 1 | 11 |  |  | 28 |  |  | .0078 | ANALOG | MELTC1ANALOG | 172.16.3.81 | 1 | 21
07219 | ME | KWPHR1 | ME PREVIOUS HOUR DEMAND | 1 | 11 |  |  | 12 |  |  | 144 | ANALOG | MEKWPHR1ANALOG | 172.16.3.81 | 1 | 36
07699 | ME | P2 | MELROSE ACCUMULATOR CEC | 1 | 11 | 1 | [5 empty] | PULSE | MEP2PULSE | 172.16.3.81 | 1 | #N/A
07733 | ME | MV1- | ME VARS LEAD | 1 | 11 |  |  | 11 |  |  | 48 | ANALOG | MEMV1-ANALOG | 172.16.3.81 | 1 | 33
07757 | ME | MV1 | ME VARS LAG | 1 | 11 |  |  | 10 |  |  | 48 | ANALOG | MEMV1ANALOG | 172.16.3.81 | 1 | 32
07759 | ME | DCV | ME DC VOLTS | 1 | 11 |  |  | 29 |  |  | .07327797 | ANALOG | MEDCVANALOG | 172.16.3.81 | 1 | 70
07760 | ME | 1PF | ME FDR 1 POWER FACTOR | 1 | 11 |  |  | 36 |  |  | 0.1 | ANALOG | ME1PFANALOG | 172.16.3.81 | 1 | 51
07773 | ME | 2PF | ME FDR 2 POWER FACTOR | 1 | 11 |  |  | 37 |  |  | 0.1 | ANALOG | ME2PFANALOG | 172.16.3.81 | 1 | 57
08081 | ME | THST1 | ME TX WINDING 1 TEMP | 1 | 11 |  |  | 40 |  |  | 1 | ANALOG | METHST1ANALOG | 172.16.3.81 | 1 | 38
08082 | ME | THST2 | ME TX WINDING 2 TEMP | 1 | 11 |  |  | 41 |  |  | 1 | ANALOG | METHST2ANALOG | 172.16.3.81 | 1 | 39
08083 | ME | THST3 | ME TX WINDING 3 TEMP | 1 | 11 |  |  | 42 |  |  | 1 | ANALOG | METHST3ANALOG | 172.16.3.81 | 1 | 40
08084 | ME | TXTEMP | ME TX TANK OIL TEMP | 1 | 11 |  |  | 43 |  |  | 1 | ANALOG | METXTEMPANALOG | 172.16.3.81 | 1 | 41
08371 | ME | TCTEMP | ME LTC TANK OIL TEMP | 1 | 11 |  |  | 44 |  |  | 1 | ANALOG | METCTEMPANALOG | 172.16.3.81 | 1 | 42
08405 | ME | TXABT | ME TX AMBIENT TEMP | 1 | 11 |  |  | 45 |  |  | 1 | ANALOG | METXABTANALOG | 172.16.3.81 | 1 | 43
35032 | ME | TC | TX LTC RAISE | 1 | 11 |  |  |  | 23 | 1 |  | RELAY | METCRELAY | 172.16.3.81 | 1 | 11
35032 | ME | TC | TX LTC LOWER | 1 | 11 |  |  |  | 23 | 0 |  | RELAY | METCRELAY | 172.16.3.81 | 1 | 11

## Status
Tag Name | Point Number (RTU)
QEIA_DNP._K697 | 0 | K697 | 0
QEIA_DNP._T1F1AC | 31 | T1F1AC | 31
QEIA_DNP._T1F2AC | 32 | T1F2AC | 32
QEIA_DNP._TX1NHI | 33 | TX1NHI | 33
QEIA_DNP._TX1NLO | 34 | TX1NLO | 34
QEIA_DNP._T1NCLO | 35 | T1NCLO | 35
QEIA_DNP._T1PR | 36 | T1PR | 36
QEIA_DNP._T1SP | 37 | T1SP | 37
QEIA_DNP._TX1LO | 38 | TX1LO | 38
QEIA_DNP._TX1HI | 39 | TX1HI | 39
QEIA_DNP._LTC1LO | 41 | LTC1LO | 41
QEIA_DNP._TC1PWR | 42 | TC1PWR | 42
QEIA_DNP._TCP1 | 43 | TCP1 | 43
QEIA_DNP._LTCMT1 | 44 | LTCMT1 | 44
QEIA_DNP._TCPR1 | 45 | TCPR1 | 45
QEIA_DNP._86X1 | 46 | 86X1 | 46
QEIA_DNP._T1FAN1 | 47 | T1FAN1 | 47
QEIA_DNP._T1FAN2 | 48 | T1FAN2 | 48
QEIA_DNP._TX1TOT | 49 | TX1TOT | 49
QEIA_DNP._TX1HS | 50 | TX1HS | 50
QEIA_DNP._TX1LR | 51 | TX1LR | 51
QEIA_DNP._TX1K1 | 52 | TX1K1 | 52
QEIA_DNP._TX1K2 | 53 | TX1K2 | 53
QEIA_DNP._TCA1 | 54 | TCA1 | 54
QEIA_DNP._T1HIAL | 56 | T1HIAL | 56
QEIA_DNP._S3L12 | 64 | S3L12 | 64
QEIA_DNP._1 | 66 | 1 | 66
QEIA_DNP._1R | 67 | 1R | 67
QEIA_DNP._1GT | 68 | 1GT | 68
QEIA_DNP._1LR | 69 | 1LR | 69
QEIA_DNP._1UF | 70 | 1UF | 70
QEIA_DNP._1BF | 71 | 1BF | 71
QEIA_DNP._1HL | 72 | 1HL | 72
QEIA_DNP._1POT | 73 | 1POT | 73
QEIA_DNP._79LO1 | 74 | 79LO1 | 74
QEIA_DNP._2 | 78 | 2 | 78
QEIA_DNP._2R | 79 | 2R | 79
QEIA_DNP._2GT | 80 | 2GT | 80
QEIA_DNP._2LR | 81 | 2LR | 81
QEIA_DNP._2UF | 82 | 2UF | 82
QEIA_DNP._2BF | 83 | 2BF | 83
QEIA_DNP._2HL | 84 | 2HL | 84
QEIA_DNP._2POT | 85 | 2POT | 85
QEIA_DNP._79LO2 | 86 | 79LO2 | 86
QEIA_DNP._3 | 90 | 3 | 90
QEIA_DNP._3R | 91 | 3R | 91
QEIA_DNP._3GT | 92 | 3GT | 92
QEIA_DNP._3LR | 93 | 3LR | 93
QEIA_DNP._3UF | 94 | 3UF | 94
QEIA_DNP._3BF | 95 | 3BF | 95
QEIA_DNP._3HL | 96 | 3HL | 96
QEIA_DNP._3POT | 97 | 3POT | 97
QEIA_DNP._79LO3 | 98 | 79LO3 | 98
QEIA_DNP._4 | 102 | 4 | 102
QEIA_DNP._4R | 103 | 4R | 103
QEIA_DNP._4GT | 104 | 4GT | 104
QEIA_DNP._4LR | 105 | 4LR | 105
QEIA_DNP._4BF | 107 | 4BF | 107
QEIA_DNP._4HL | 108 | 4HL | 108
QEIA_DNP._4POT | 109 | 4POT | 109
QEIA_DNP._79LO4 | 110 | 79LO4 | 110
QEIA_DNP._35C101 | 114 | 35C101 | 114
QEIA_DNP._35C102 | 115 | 35C102 | 115
QEIA_DNP._35C103 | 116 | 35C103 | 116
QEIA_DNP._35C104 | 117 | 35C104 | 117
QEIA_DNP._35C106 | 119 | 35C106 | 119
QEIA_DNP._MET1CP | 121 | MET1CP | 121
QEIA_DNP._35C109 | 122 | 35C109 | 122
QEIA_DNP._35C110 | 123 | 35C110 | 123
QEIA_DNP._35C111 | 124 | 35C111 | 124
QEIA_DNP._35C118 | 131 | 35C118 | 131
QEIA_DNP._35C119 | 132 | 35C119 | 132
QEIA_DNP._35C120 | 133 | 35C120 | 133
QEIA_DNP._35C121 | 134 | 35C121 | 134
QEIA_DNP._35C123 | 136 | 35C123 | 136
QEIA_DNP._35C126 | 139 | 35C126 | 139
QEIA_DNP._35C128 | 141 | 35C128 | 141
QEIA_DNP._387SC1 | 171 | 387SC1 | 171
QEIA_DNP._501SC1 | 172 | 501SC1 | 172
QEIA_DNP._21T1SC | 175 | 21T1SC | 175
QEIA_DNP._MET1SC | 176 | MET1SC | 176
QEIA_DNP._2407SC | 177 | 2407SC | 177
QEIA_DNP._25SC10 | 181 | 25SC10 | 181
QEIA_DNP._24T1SC | 184 | 24T1SC | 184
QEIA_DNP._351SC1 | 188 | 351SC1 | 188
QEIA_DNP._351SC2 | 189 | 351SC2 | 189
QEIA_DNP._351SC3 | 190 | 351SC3 | 190
QEIA_DNP._351SC4 | 191 | 351SC4 | 191
QEIA_DNP._LRS | 193 | LRS | 193
QEIA_DNP._TX1DRD | 194 | TX1DRD | 194
QEIA_DNP._86T1 | 195 | 86T1 | 195
QEIA_DNP._86TCM1 | 196 | 86TCM1 | 196
QEIA_DNP._94TCM1 | 201 | 94TCM1 | 201
QEIA_DNP._FANHYD | 208 | FANHYD | 208
QEIA_DNP._SMOKE | 209 | SMOKE | 209
QEIA_DNP._BATPWR | 210 | BATPWR | 210
QEIA_DNP._BATTDC | 211 | BATTDC | 211
QEIA_DNP._BATGND | 212 | BATGND | 212

## Controls
QEI MASTER POINT | Tag Name | Point Number (RTU/RTAC)
25T (Trip) | K697 | 0
25C (Close) | K697
19T | T1FAN1 | 6
19C | T1FAN1
20T | T1FAN2 | 7
20C | T1FAN2
21T | TCA1 | 8
21C | TCA1
22T | TX1K1 | 9
22C | TX1K1
23T | TX1K2 | 10
23C | TX1K2
24T | TC1 | 11
24C | TC1
18T | S3L12 | 17
18C | S3L12
1T | 1 | 18
1C | 1
2T | 1R | 19
2C | 1R
3T | 1GT | 20
3C | 1GT
4T | 1HL | 21
4C | 1HL
5T | 2 | 23
5C | 2
6T | 2R | 24
6C | 2R
7T | 2GT | 25
7C | 2GT
8T | 2HL | 26
8C | 2HL
9T | 3 | 28
9C | 3
10T | 3R | 29
10C | 3R
11T | 3GT | 30
11C | 3GT
12T | 3HL | 31
12C | 3HL
13T | 4 | 33
13C | 4
14T | 4R | 34
14C | 4R
15T | 4GT | 35
15C | 4GT
16T | 4HL | 36
16C | 4HL

## Analogs
Tag Name | RTU Point
QEIA_DNP._LTC1 | 21 | LTC1 | 21
QEIA_DNP._RAV1 | 24 | RAV1 | 24
QEIA_DNP._RBV1 | 25 | RBV1 | 25
QEIA_DNP._RCV1 | 26 | RCV1 | 26
QEIA_DNP._TX1A | 27 | TX1A | 27
QEIA_DNP._TX1B | 28 | TX1B | 28
QEIA_DNP._TX1C | 29 | TX1C | 29
QEIA_DNP._KVA1M | 30 | KVA1M | 30
QEIA_DNP._TX1W | 31 | TX1W | 31
QEIA_DNP._MV1LAG | 32 | MV1LAG | 32
QEIA_DNP._MV1LEAD | 33 | MV1LEAD | 33
QEIA_DNP._PF1M | 34 | PF1M | 34
QEIA_DNP._TX1FRQ | 35 | TX1FRQ | 35
QEIA_DNP._KWPHR1 | 36 | KWPHR1 | 36
QEIA_DNP._THST1 | 38 | THST1 | 38
QEIA_DNP._THST2 | 39 | THST2 | 39
QEIA_DNP._THST3 | 40 | THST3 | 40
QEIA_DNP._TXTEMP | 41 | TXTEMP | 41
QEIA_DNP._TCTEMP | 42 | TCTEMP | 42
QEIA_DNP._TXABT | 43 | TXABT | 43
QEIA_DNP._1A | 46 | 1A | 46
QEIA_DNP._1B | 47 | 1B | 47
QEIA_DNP._1C | 48 | 1C | 48
QEIA_DNP._1KW | 49 | 1KW | 49
QEIA_DNP._1PF | 51 | 1PF | 51
QEIA_DNP._2A | 52 | 2A | 52
QEIA_DNP._2B | 53 | 2B | 53
QEIA_DNP._2C | 54 | 2C | 54
QEIA_DNP._2KW | 55 | 2KW | 55
QEIA_DNP._2PF | 57 | 2PF | 57
QEIA_DNP._3A | 58 | 3A | 58
QEIA_DNP._3B | 59 | 3B | 59
QEIA_DNP._3C | 60 | 3C | 60
QEIA_DNP._3KW | 61 | 3KW | 61
QEIA_DNP._3PF | 63 | 3PF | 63
QEIA_DNP._4A | 64 | 4A | 64
QEIA_DNP._4B | 65 | 4B | 65
QEIA_DNP._4C | 66 | 4C | 66
QEIA_DNP._4KW | 67 | 4KW | 67
QEIA_DNP._4PF | 69 | 4PF | 69
QEIA_DNP._DCV | 70 | DCV | 70

## Combined
Tag Name | Point Number (RTU) | [5 empty] | BACK CHECK
QEIA_DNP._K697 | 0 | MEK697STATUS | STATUS | STATUS | K697 | 0 | TRUE
QEIA_DNP._T1F1AC | 31 | MET1F1ACSTATUS | STATUS | STATUS | T1F1AC | 31 | TRUE
QEIA_DNP._T1F2AC | 32 | MET1F2ACSTATUS | STATUS | STATUS | T1F2AC | 32 | TRUE
QEIA_DNP._TX1NHI | 33 | METX1NHISTATUS | STATUS | STATUS | TX1NHI | 33 | TRUE
QEIA_DNP._TX1NLO | 34 | METX1NLOSTATUS | STATUS | STATUS | TX1NLO | 34 | TRUE
QEIA_DNP._T1NCLO | 35 | MET1NCLOSTATUS | STATUS | STATUS | T1NCLO | 35 | TRUE
QEIA_DNP._T1PR | 36 | MET1PRSTATUS | STATUS | STATUS | T1PR | 36 | TRUE
QEIA_DNP._T1SP | 37 | MET1SPSTATUS | STATUS | STATUS | T1SP | 37 | TRUE
QEIA_DNP._TX1LO | 38 | METX1LOSTATUS | STATUS | STATUS | TX1LO | 38 | TRUE
QEIA_DNP._TX1HI | 39 | METX1HISTATUS | STATUS | STATUS | TX1HI | 39 | TRUE
QEIA_DNP._LTC1LO | 41 | MELTC1LOSTATUS | STATUS | STATUS | LTC1LO | 41 | TRUE
QEIA_DNP._TC1PWR | 42 | METC1PWRSTATUS | STATUS | STATUS | TC1PWR | 42 | TRUE
QEIA_DNP._TCP1 | 43 | METCP1STATUS | STATUS | STATUS | TCP1 | 43 | TRUE
QEIA_DNP._LTCMT1 | 44 | MELTCMT1STATUS | STATUS | STATUS | LTCMT1 | 44 | TRUE
QEIA_DNP._TCPR1 | 45 | METCPR1STATUS | STATUS | STATUS | TCPR1 | 45 | TRUE
QEIA_DNP._86X1 | 46 | ME86X1STATUS | STATUS | STATUS | 86X1 | 46 | TRUE
QEIA_DNP._T1FAN1 | 47 | MET1FAN1STATUS | STATUS | STATUS | T1FAN1 | 47 | TRUE
QEIA_DNP._T1FAN2 | 48 | MET1FAN2STATUS | STATUS | STATUS | T1FAN2 | 48 | TRUE
QEIA_DNP._TX1TOT | 49 | METX1TOTSTATUS | STATUS | STATUS | TX1TOT | 49 | TRUE
QEIA_DNP._TX1HS | 50 | METX1HSSTATUS | STATUS | STATUS | TX1HS | 50 | TRUE
QEIA_DNP._TX1LR | 51 | METX1LRSTATUS | STATUS | STATUS | TX1LR | 51 | TRUE
QEIA_DNP._TX1K1 | 52 | METX1K1STATUS | STATUS | STATUS | TX1K1 | 52 | TRUE
QEIA_DNP._TX1K2 | 53 | METX1K2STATUS | STATUS | STATUS | TX1K2 | 53 | TRUE
QEIA_DNP._TCA1 | 54 | METCA1STATUS | STATUS | STATUS | TCA1 | 54 | TRUE
QEIA_DNP._T1HIAL | 56 | MET1HIALSTATUS | STATUS | STATUS | T1HIAL | 56 | TRUE
QEIA_DNP._S3L12 | 64 | MES3L12STATUS | STATUS | STATUS | S3L12 | 64 | TRUE
QEIA_DNP._1 | 66 | ME1STATUS | STATUS | STATUS | 1 | 66 | TRUE
QEIA_DNP._1R | 67 | ME1RSTATUS | STATUS | STATUS | 1R | 67 | TRUE
QEIA_DNP._1GT | 68 | ME1GTSTATUS | STATUS | STATUS | 1GT | 68 | TRUE
QEIA_DNP._1LR | 69 | ME1LRSTATUS | STATUS | STATUS | 1LR | 69 | TRUE
QEIA_DNP._1UF | 70 | ME1UFSTATUS | STATUS | STATUS | 1UF | 70 | TRUE
QEIA_DNP._1BF | 71 | ME1BFSTATUS | STATUS | STATUS | 1BF | 71 | TRUE
QEIA_DNP._1HL | 72 | ME1HLSTATUS | STATUS | STATUS | 1HL | 72 | TRUE
QEIA_DNP._1POT | 73 | ME1POTSTATUS | STATUS | STATUS | 1POT | 73 | TRUE
QEIA_DNP._79LO1 | 74 | ME79LO1STATUS | STATUS | STATUS | 79LO1 | 74 | TRUE
QEIA_DNP._2 | 78 | ME2STATUS | STATUS | STATUS | 2 | 78 | TRUE
QEIA_DNP._2R | 79 | ME2RSTATUS | STATUS | STATUS | 2R | 79 | TRUE
QEIA_DNP._2GT | 80 | ME2GTSTATUS | STATUS | STATUS | 2GT | 80 | TRUE
QEIA_DNP._2LR | 81 | ME2LRSTATUS | STATUS | STATUS | 2LR | 81 | TRUE
QEIA_DNP._2UF | 82 | ME2UFSTATUS | STATUS | STATUS | 2UF | 82 | TRUE
QEIA_DNP._2BF | 83 | ME2BFSTATUS | STATUS | STATUS | 2BF | 83 | TRUE
QEIA_DNP._2HL | 84 | ME2HLSTATUS | STATUS | STATUS | 2HL | 84 | TRUE
QEIA_DNP._2POT | 85 | ME2POTSTATUS | STATUS | STATUS | 2POT | 85 | TRUE
QEIA_DNP._79LO2 | 86 | ME79LO2STATUS | STATUS | STATUS | 79LO2 | 86 | TRUE
QEIA_DNP._3 | 90 | ME3STATUS | STATUS | STATUS | 3 | 90 | TRUE
QEIA_DNP._3R | 91 | ME3RSTATUS | STATUS | STATUS | 3R | 91 | TRUE
QEIA_DNP._3GT | 92 | ME3GTSTATUS | STATUS | STATUS | 3GT | 92 | TRUE
QEIA_DNP._3LR | 93 | ME3LRSTATUS | STATUS | STATUS | 3LR | 93 | TRUE
QEIA_DNP._3UF | 94 | ME3UFSTATUS | STATUS | STATUS | 3UF | 94 | TRUE
QEIA_DNP._3BF | 95 | ME3BFSTATUS | STATUS | STATUS | 3BF | 95 | TRUE
QEIA_DNP._3HL | 96 | ME3HLSTATUS | STATUS | STATUS | 3HL | 96 | TRUE
QEIA_DNP._3POT | 97 | ME3POTSTATUS | STATUS | STATUS | 3POT | 97 | TRUE
QEIA_DNP._79LO3 | 98 | ME79LO3STATUS | STATUS | STATUS | 79LO3 | 98 | TRUE
QEIA_DNP._4 | 102 | ME4STATUS | STATUS | STATUS | 4 | 102 | TRUE
QEIA_DNP._4R | 103 | ME4RSTATUS | STATUS | STATUS | 4R | 103 | TRUE
QEIA_DNP._4GT | 104 | ME4GTSTATUS | STATUS | STATUS | 4GT | 104 | TRUE
QEIA_DNP._4LR | 105 | ME4LRSTATUS | STATUS | STATUS | 4LR | 105 | TRUE
QEIA_DNP._4BF | 107 | ME4BFSTATUS | STATUS | STATUS | 4BF | 107 | TRUE
QEIA_DNP._4HL | 108 | ME4HLSTATUS | STATUS | STATUS | 4HL | 108 | TRUE
QEIA_DNP._4POT | 109 | ME4POTSTATUS | STATUS | STATUS | 4POT | 109 | TRUE
QEIA_DNP._79LO4 | 110 | ME79LO4STATUS | STATUS | STATUS | 79LO4 | 110 | TRUE
QEIA_DNP._35C101 | 114 | ME35C101STATUS | STATUS | STATUS | 35C101 | 114 | TRUE
QEIA_DNP._35C102 | 115 | ME35C102STATUS | STATUS | STATUS | 35C102 | 115 | TRUE
QEIA_DNP._35C103 | 116 | ME35C103STATUS | STATUS | STATUS | 35C103 | 116 | TRUE
QEIA_DNP._35C104 | 117 | ME35C104STATUS | STATUS | STATUS | 35C104 | 117 | TRUE
QEIA_DNP._35C106 | 119 | ME35C106STATUS | STATUS | STATUS | 35C106 | 119 | TRUE
QEIA_DNP._MET1CP | 121 | MEMET1CPSTATUS | STATUS | STATUS | MET1CP | 121 | TRUE
QEIA_DNP._35C109 | 122 | ME35C109STATUS | STATUS | STATUS | 35C109 | 122 | TRUE
QEIA_DNP._35C110 | 123 | ME35C110STATUS | STATUS | STATUS | 35C110 | 123 | TRUE
QEIA_DNP._35C111 | 124 | ME35C111STATUS | STATUS | STATUS | 35C111 | 124 | TRUE
QEIA_DNP._35C118 | 131 | ME35C118STATUS | STATUS | STATUS | 35C118 | 131 | TRUE
QEIA_DNP._35C119 | 132 | ME35C119STATUS | STATUS | STATUS | 35C119 | 132 | TRUE
QEIA_DNP._35C120 | 133 | ME35C120STATUS | STATUS | STATUS | 35C120 | 133 | TRUE
QEIA_DNP._35C121 | 134 | ME35C121STATUS | STATUS | STATUS | 35C121 | 134 | TRUE
QEIA_DNP._35C123 | 136 | ME35C123STATUS | STATUS | STATUS | 35C123 | 136 | TRUE
QEIA_DNP._35C126 | 139 | ME35C126STATUS | STATUS | STATUS | 35C126 | 139 | TRUE
QEIA_DNP._35C128 | 141 | ME35C128STATUS | STATUS | STATUS | 35C128 | 141 | TRUE
QEIA_DNP._387SC1 | 171 | ME387SC1STATUS | STATUS | STATUS | 387SC1 | 171 | TRUE
QEIA_DNP._501SC1 | 172 | ME501SC1STATUS | STATUS | STATUS | 501SC1 | 172 | TRUE
QEIA_DNP._21T1SC | 175 | ME21T1SCSTATUS | STATUS | STATUS | 21T1SC | 175 | TRUE
QEIA_DNP._MET1SC | 176 | MEMET1SCSTATUS | STATUS | STATUS | MET1SC | 176 | TRUE
QEIA_DNP._2407SC | 177 | ME2407SCSTATUS | STATUS | STATUS | 2407SC | 177 | TRUE
QEIA_DNP._25SC10 | 181 | ME25SC10STATUS | STATUS | STATUS | 25SC10 | 181 | TRUE
QEIA_DNP._24T1SC | 184 | ME24T1SCSTATUS | STATUS | STATUS | 24T1SC | 184 | TRUE
QEIA_DNP._351SC1 | 188 | ME351SC1STATUS | STATUS | STATUS | 351SC1 | 188 | TRUE
QEIA_DNP._351SC2 | 189 | ME351SC2STATUS | STATUS | STATUS | 351SC2 | 189 | TRUE
QEIA_DNP._351SC3 | 190 | ME351SC3STATUS | STATUS | STATUS | 351SC3 | 190 | TRUE
QEIA_DNP._351SC4 | 191 | ME351SC4STATUS | STATUS | STATUS | 351SC4 | 191 | TRUE
QEIA_DNP._LRS | 193 | MELRSSTATUS | STATUS | STATUS | LRS | 193 | TRUE
QEIA_DNP._TX1DRD | 194 | METX1DRDSTATUS | STATUS | STATUS | TX1DRD | 194 | TRUE
QEIA_DNP._86T1 | 195 | ME86T1STATUS | STATUS | STATUS | 86T1 | 195 | TRUE
QEIA_DNP._86TCM1 | 196 | ME86TCM1STATUS | STATUS | STATUS | 86TCM1 | 196 | TRUE
QEIA_DNP._94TCM1 | 201 | ME94TCM1STATUS | STATUS | STATUS | 94TCM1 | 201 | TRUE
QEIA_DNP._FANHYD | 208 | MEFANHYDSTATUS | STATUS | STATUS | FANHYD | 208 | TRUE
QEIA_DNP._SMOKE | 209 | MESMOKESTATUS | STATUS | STATUS | SMOKE | 209 | TRUE
QEIA_DNP._BATPWR | 210 | MEBATPWRSTATUS | STATUS | STATUS | BATPWR | 210 | TRUE
QEIA_DNP._BATTDC | 211 | MEBATTDCSTATUS | STATUS | STATUS | BATTDC | 211 | TRUE
QEIA_DNP._BATGND | 212 | MEBATGNDSTATUS | STATUS | STATUS | BATGND | 212 | TRUE
QEIA_DNP._LTC1 | 21 | MELTC1ANALOG | ANALOG | ANALOG | LTC1 | 21 | TRUE
QEIA_DNP._RAV1 | 24 | MERAV1ANALOG | ANALOG | ANALOG | RAV1 | 24 | TRUE
QEIA_DNP._RBV1 | 25 | MERBV1ANALOG | ANALOG | ANALOG | RBV1 | 25 | TRUE
QEIA_DNP._RCV1 | 26 | MERCV1ANALOG | ANALOG | ANALOG | RCV1 | 26 | TRUE
QEIA_DNP._TX1A | 27 | METX1AANALOG | ANALOG | ANALOG | TX1A | 27 | TRUE
QEIA_DNP._TX1B | 28 | METX1BANALOG | ANALOG | ANALOG | TX1B | 28 | TRUE
QEIA_DNP._TX1C | 29 | METX1CANALOG | ANALOG | ANALOG | TX1C | 29 | TRUE
QEIA_DNP._KVA1M | 30 | MEKVA1MANALOG | ANALOG | ANALOG | KVA1M | 30 | TRUE
QEIA_DNP._TX1W | 31 | METX1WANALOG | ANALOG | ANALOG | TX1W | 31 | TRUE
QEIA_DNP._MV1 | 32 | MEMV1ANALOG | ANALOG | ANALOG | MV1 | 32 | TRUE
QEIA_DNP._MV1- | 33 | MEMV1-ANALOG | ANALOG | ANALOG | MV1- | 33 | TRUE
QEIA_DNP._PF1M | 34 | MEPF1MANALOG | ANALOG | ANALOG | PF1M | 34 | TRUE
QEIA_DNP._TX1FRQ | 35 | METX1FRQANALOG | ANALOG | ANALOG | TX1FRQ | 35 | TRUE
QEIA_DNP._KWPHR1 | 36 | MEKWPHR1ANALOG | ANALOG | ANALOG | KWPHR1 | 36 | TRUE
QEIA_DNP._THST1 | 38 | METHST1ANALOG | ANALOG | ANALOG | THST1 | 38 | TRUE
QEIA_DNP._THST2 | 39 | METHST2ANALOG | ANALOG | ANALOG | THST2 | 39 | TRUE
QEIA_DNP._THST3 | 40 | METHST3ANALOG | ANALOG | ANALOG | THST3 | 40 | TRUE
QEIA_DNP._TXTEMP | 41 | METXTEMPANALOG | ANALOG | ANALOG | TXTEMP | 41 | TRUE
QEIA_DNP._TCTEMP | 42 | METCTEMPANALOG | ANALOG | ANALOG | TCTEMP | 42 | TRUE
QEIA_DNP._TXABT | 43 | METXABTANALOG | ANALOG | ANALOG | TXABT | 43 | TRUE
QEIA_DNP._1A | 46 | ME1AANALOG | ANALOG | ANALOG | 1A | 46 | TRUE
QEIA_DNP._1B | 47 | ME1BANALOG | ANALOG | ANALOG | 1B | 47 | TRUE
QEIA_DNP._1C | 48 | ME1CANALOG | ANALOG | ANALOG | 1C | 48 | TRUE
QEIA_DNP._1KW | 49 | ME1KWANALOG | ANALOG | ANALOG | 1KW | 49 | TRUE
QEIA_DNP._1PF | 51 | ME1PFANALOG | ANALOG | ANALOG | 1PF | 51 | TRUE
QEIA_DNP._2A | 52 | ME2AANALOG | ANALOG | ANALOG | 2A | 52 | TRUE
QEIA_DNP._2B | 53 | ME2BANALOG | ANALOG | ANALOG | 2B | 53 | TRUE
QEIA_DNP._2C | 54 | ME2CANALOG | ANALOG | ANALOG | 2C | 54 | TRUE
QEIA_DNP._2KW | 55 | ME2KWANALOG | ANALOG | ANALOG | 2KW | 55 | TRUE
QEIA_DNP._2PF | 57 | ME2PFANALOG | ANALOG | ANALOG | 2PF | 57 | TRUE
QEIA_DNP._3A | 58 | ME3AANALOG | ANALOG | ANALOG | 3A | 58 | TRUE
QEIA_DNP._3B | 59 | ME3BANALOG | ANALOG | ANALOG | 3B | 59 | TRUE
QEIA_DNP._3C | 60 | ME3CANALOG | ANALOG | ANALOG | 3C | 60 | TRUE
QEIA_DNP._3KW | 61 | ME3KWANALOG | ANALOG | ANALOG | 3KW | 61 | TRUE
QEIA_DNP._3PF | 63 | ME3PFANALOG | ANALOG | ANALOG | 3PF | 63 | TRUE
QEIA_DNP._4A | 64 | ME4AANALOG | ANALOG | ANALOG | 4A | 64 | TRUE
QEIA_DNP._4B | 65 | ME4BANALOG | ANALOG | ANALOG | 4B | 65 | TRUE
QEIA_DNP._4C | 66 | ME4CANALOG | ANALOG | ANALOG | 4C | 66 | TRUE
QEIA_DNP._4KW | 67 | ME4KWANALOG | ANALOG | ANALOG | 4KW | 67 | TRUE
QEIA_DNP._4PF | 69 | ME4PFANALOG | ANALOG | ANALOG | 4PF | 69 | TRUE
QEIA_DNP._DCV | 70 | MEDCVANALOG | ANALOG | ANALOG | DCV | 70 | TRUE
|  | MEK697RELAY | RELAY | 25T (Trip) | K697 | 0 | TRUE
|  | MEK697RELAY | RELAY | 25C (Close) | K697 |  | TRUE
|  | MET1FAN1RELAY | RELAY | 19T | T1FAN1 | 6 | TRUE
|  | MET1FAN1RELAY | RELAY | 19C | T1FAN1 |  | TRUE
|  | MET1FAN2RELAY | RELAY | 20T | T1FAN2 | 7 | TRUE
|  | MET1FAN2RELAY | RELAY | 20C | T1FAN2 |  | TRUE
|  | METCA1RELAY | RELAY | 21T | TCA1 | 8 | TRUE
|  | METCA1RELAY | RELAY | 21C | TCA1 |  | TRUE
|  | METX1K1RELAY | RELAY | 22T | TX1K1 | 9 | TRUE
|  | METX1K1RELAY | RELAY | 22C | TX1K1 |  | TRUE
|  | METX1K2RELAY | RELAY | 23T | TX1K2 | 10 | TRUE
|  | METX1K2RELAY | RELAY | 23C | TX1K2 |  | TRUE
|  | METCRELAY | RELAY | 24T | TC | 11 | TRUE
|  | METCRELAY | RELAY | 24C | TC |  | TRUE
|  | MES3L12RELAY | RELAY | 18T | S3L12 | 17 | TRUE
|  | MES3L12RELAY | RELAY | 18C | S3L12 |  | TRUE
|  | ME1RELAY | RELAY | 1T | 1 | 18 | TRUE
|  | ME1RELAY | RELAY | 1C | 1 |  | TRUE
|  | ME1RRELAY | RELAY | 2T | 1R | 19 | TRUE
|  | ME1RRELAY | RELAY | 2C | 1R |  | TRUE
|  | ME1GTRELAY | RELAY | 3T | 1GT | 20 | TRUE
|  | ME1GTRELAY | RELAY | 3C | 1GT |  | TRUE
|  | ME1HLRELAY | RELAY | 4T | 1HL | 21 | TRUE
|  | ME1HLRELAY | RELAY | 4C | 1HL |  | TRUE
|  | ME2RELAY | RELAY | 5T | 2 | 23 | TRUE
|  | ME2RELAY | RELAY | 5C | 2 |  | TRUE
|  | ME2RRELAY | RELAY | 6T | 2R | 24 | TRUE
|  | ME2RRELAY | RELAY | 6C | 2R |  | TRUE
|  | ME2GTRELAY | RELAY | 7T | 2GT | 25 | TRUE
|  | ME2GTRELAY | RELAY | 7C | 2GT |  | TRUE
|  | ME2HLRELAY | RELAY | 8T | 2HL | 26 | TRUE
|  | ME2HLRELAY | RELAY | 8C | 2HL |  | TRUE
|  | ME3RELAY | RELAY | 9T | 3 | 28 | TRUE
|  | ME3RELAY | RELAY | 9C | 3 |  | TRUE
|  | ME3RRELAY | RELAY | 10T | 3R | 29 | TRUE
|  | ME3RRELAY | RELAY | 10C | 3R |  | TRUE
|  | ME3GTRELAY | RELAY | 11T | 3GT | 30 | TRUE
|  | ME3GTRELAY | RELAY | 11C | 3GT |  | TRUE
|  | ME3HLRELAY | RELAY | 12T | 3HL | 31 | TRUE
|  | ME3HLRELAY | RELAY | 12C | 3HL |  | TRUE
|  | ME4RELAY | RELAY | 13T | 4 | 33 | TRUE
|  | ME4RELAY | RELAY | 13C | 4 |  | TRUE
|  | ME4RRELAY | RELAY | 14T | 4R | 34 | TRUE
|  | ME4RRELAY | RELAY | 14C | 4R |  | TRUE
|  | ME4GTRELAY | RELAY | 15T | 4GT | 35 | TRUE
|  | ME4GTRELAY | RELAY | 15C | 4GT |  | TRUE
|  | ME4HLRELAY | RELAY | 16T | 4HL | 36 | TRUE
|  | ME4HLRELAY | RELAY | 16C | 4HL |  | TRUE